## Mode
Mode ( 0 : AC / DC Hybrid, 1 : AC only, 2 : DC only)
0

## AC Bus Data
Bus | Gs[MW] | Bs[Mvar] | Z_p | I_p | P_p | Z_q | I_q | P_q | k_pw | k_qw | V0 [pu] | Va [°] | V_base [V] | V_min [pu] | V_max [pu] | Area
1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1.05 | 0 | 22900 | 0.907 | 1.039 | 1
2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 22900 | 0.907 | 1.039 | 1
3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 22900 | 0.907 | 1.039 | 1
4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 22900 | 0.907 | 1.039 | 1
5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 22900 | 0.907 | 1.039 | 1
6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 22900 | 0.907 | 1.039 | 1
7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 22900 | 0.907 | 1.039 | 1
8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 22900 | 0.907 | 1.039 | 1
9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 22900 | 0.907 | 1.039 | 1
10 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 22900 | 0.907 | 1.039 | 1
11 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 22900 | 0.907 | 1.039 | 1
12 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 22900 | 0.907 | 1.039 | 1
13 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 22900 | 0.907 | 1.039 | 1
14 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 22900 | 0.907 | 1.039 | 1

## AC Line Data
Line # | From | To | R [Ω] | X [Ω] | B [S] | Tap ratio | angle(°) | rateA [MVA] | rateB [MVA] | rateC [MVA] | AC Transformer status (0/1) | connection status (0/1)
1 | 1 | 2 | 1.4382 | 1.0321 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 1
2 | 2 | 3 | 2.2542 | 1.6177 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 1
3 | 3 | 4 | 0.3111 | 0.22326 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 1
4 | 4 | 5 | 0.2856 | 0.20496 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 1
5 | 5 | 6 | 0.7854 | 0.56364 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 1
6 | 6 | 7 | 0.1224 | 0.08784 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 1
7 | 7 | 8 | 0.8517 | 0.61122 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 1
8 | 8 | 9 | 0.1632 | 0.11712 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 1
9 | 9 | 10 | 0.3927 | 0.28182 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 1
10 | 10 | 11 | 0.1683 | 0.12078 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 1
11 | 4 | 11 | 0.2499 | 0.17934 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 1
12 | 3 | 8 | 0.663 | 0.4758 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 1
13 | 12 | 13 | 2.4499 | 3.5012 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 1
14 | 13 | 14 | 1.498 | 2.1408 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 1
15 | 8 | 14 | 1.002 | 1.432 | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 1
1->10
10 -> 100

## AC 3w Transformer Data
3w trans # | Bus 1 | Bus 2 | Bus 3 | status (0/1) | Vn1 [kV] | Vn2 [kV] | Vn3 [kV] | Sn1 [MVA] | Sn2 [MVA] | Sn3 [MVA] | r12 | r23 | r31 | x12 | x23 | x31 | vk12 [%] | vk23 [%] | vk31 [%] | vkr12 [%] | vkr23 [%] | vkr31 [%] | tap side | tap ratio | shift_deg MV [degree] | shift_deg LV [degree] | pfe [kW] | i0 [%] | winding map

## AC Gen Data
Bus_No | AC Gen Type (No Gen : 0/AC Trans : 1/ Syn Gen : 2/IBR : 3) | AC Gen Mode (PQ Mode : 0/Droop Mode : 1/ PV Mode : 2/Slack : 3) Same Bus = Same Gen Mode | Droop (P-f) [%] | Droop (Q-Vac) [%] | P_gen [W] | Q_gen [Var] | Vg [pu] (If Gen PV mode or Droop mode) | Status (미반영) | Local Sbase [MVA] | ¦V¦ deadband (±) [pu]
1 | 1 | 3 | - | - | 0 | 0 | 1.05 | 1 | 250 | 0
((𝑓𝑟𝑒𝑞_𝑝𝑢)/𝑃_𝑝𝑢 ×100)
(𝑉_(𝐴𝐶,𝑝𝑢)/𝑄_𝑝𝑢 ×100)

## AC P Consume Data
Bus / 시각 | 1
1 | 0
2 | 0
3 | 225250
4 | -20000
5 | -630000
6 | -30000
7 | 76500
8 | 0
9 | 573750
10 | 68000
11 | -10000
12 | 0
13 | 34000
14 | 331500

## AC Q Consume Data
Bus / 시각 | 1
1 | 0
2 | 0
3 | 139597.412
4 | 0
5 | 0
6 | 0
7 | 47410.442
8 | 0
9 | 355578.3
10 | 42142.62
11 | 0
12 | 0
13 | 21071.3108
14 | 205445.248

## DC Bus Data
Bus | Nominal Current | V0 [pu] | V_base [V] | VM min [pu] | VM max [pu]
15 | 0 | 1 | 35000 | 0.95 | 1.05
16 | 0 | 1 | 35000 | 0.95 | 1.05
17 | 0 | 1 | 35000 | 0.95 | 1.05
18 | 0 | 1 | 35000 | 0.95 | 1.05
19 | 0 | 1 | 35000 | 0.95 | 1.05
20 | 0 | 1 | 35000 | 0.95 | 1.05
21 | 0 | 1 | 35000 | 0.95 | 1.05
22 | 0 | 1 | 750 | 0.95 | 1.05
23 | 0 | 1 | 750 | 0.95 | 1.05
24 | 0 | 1 | 750 | 0.95 | 1.05
25 | 0 | 1 | 750 | 0.95 | 1.05

## DC Line Data
Line # | From | To | R [Ω] | rateA [MVA] | rateB [MVA] | rateC [MVA] | connection status (0/1)
1 | 15 | 16 | 2.004 | 10 | 10 | 10 | 1
2 | 16 | 17 | 2.505 | 10 | 10 | 10 | 1
3 | 17 | 19 | 3.507 | 10 | 10 | 10 | 1
4 | 19 | 20 | 1.503 | 10 | 10 | 10 | 1
5 | 20 | 21 | 2.004 | 10 | 10 | 10 | 1
6 | 18 | 21 | 0.501 | 10 | 10 | 10 | 1
7 | 22 | 23 | 0.248 | 10 | 10 | 10 | 1
8 | 23 | 24 | 0.1984 | 10 | 10 | 10 | 1
9 | 24 | 25 | 0.124 | 10 | 10 | 10 | 1
18 -> 180

## DC Gen Data
Bus_No | DC Gen Type (No Gen : 0/IBR : 1/ ESS : 2/Fuel Cell :3 / Generator : 4) | DC Gen Mode (P: Mode : 0/Droop Mode : 1/ CV Mode : 2) Same Bus = Same Gen Mode | Droop (P-Vdc) [%] | P_gen [W] | Vg [pu] (If Gen PV mode or Droop mode) | Status (미반영) | Local Sbase [MVA] | ¦V¦ deadband (±) [pu]
(𝑉_(𝐷𝐶,𝑝𝑢)/𝑃_𝑝𝑢 ×100)

## DC P Consume Data
Bus / 시각 | 1
15 | 0
16 | 1000000
17 | 0
18 | 0
19 | 3000000
20 | 1000000
21 | 0
22 | 0
23 | 100000
24 | -100000
25 | 100000

## ACDC IC Data
From(AC) | To(DC) | AC Control Mode ( 0: CQ / 1 : Droop / 2 : CV ) | DC Control Mode ( 0: CP / 1 : Droop / 2 : CV ) | Droop Coefficient (f-P) [%] | Droop Coefficient (P-Vdc) [%] | Droop Coefficient (Q-Vac) [%] | P Operating Point [W] | Q Operating Point [Var] | rateA [MVA] | Rtf [pu] | Xtf [pu] | Bf [pu] | Rc [pu] | Xc [pu] | Status ( 0 : off / 1 : on ) | LossA | LossB | LossC rec | LossC inv
2 | 15 | 0 | 2 | - | - | - | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
6 | 17 | 0 | 2 | - | - | - | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
12 | 21 | 0 | 2 | - | - | - | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
((𝑓𝑟𝑒𝑞_𝑛𝑜𝑟𝑚)/𝑃_𝑝𝑢 ×100)
(𝑉_(𝐷𝐶.𝑛𝑜𝑟𝑚)/𝑃_𝑝𝑢 ×100)
(𝑉_(𝐴𝐶.𝑝𝑢)/𝑄_𝑝𝑢 ×100)

## MVDC LVDC Converter Data
From (MVDC) | To (LVDC) | Efficiency Curve (C0) | Efficiency Curve (C1) | Efficiency Curve (C2) | Droop Coefficient (P) MVDC VM_norm | Droop Coefficient (P) LVDC VM_norm | Operating Point (P) | rateA [MVA] | Control Mode (Off : 0 / CV(LVDC) : 1 / CP:2)
18 | 22 | 0 | 0 | 0 | 0 | 1000000000 | 0 | 10 | 1

## Sbase,frequency
S_base [MVA] | freq_base [Hz] | f_0 [pu] | freq_min [pu] | freq_max[pu] | Frequency Control Mode ( 0 : Variable / 1 : Constant ) | freq_deadband(±) [Hz]
25 | 60 | 1 | 0.95 | 1.05 | 0 | 0.036